Motion Fast 82KW Charger Fuse Failure SOP

1. Fault Name:Fuse failure
2. Fault code:without
3. Fault phenomenon:Unable to charge, the screen reports the fault
4. Cause of failure:Fuse failure
5. Applicable models:Motion Fast 82kW
6. Troubleshooting steps:
	procedure
	Contents
	Example (picture or reference file)

	Step1
	Disconnect the AC contactor of DC pile, and measure the on-off condition of the fuse by using the buzzer gear of multimeter.
If there is a beeping sound, the fuse is normal.
If there is no beeping sound, it means that the fuse is damaged, and execute Step2;
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	Step2
	Use a 13MM wrench to remove the fuse;
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	Step3
	After replacing the new fuse, repeat Step1 to measure whether the new fuse is conductive.
If it is turned on, carry out a charging test again; If it is still not connected, please contact the local after-sales service team to handle it.
If charging is normal, the device will return to normal;
If the charging is still abnormal, please contact the local after-sales service team.
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