Motion Fast 82KW Charger Fuse Failure SOP

- Fault Name:Fuse failure

- Fault code:without

- Fault phenomenon:Unable to charge, the screen reports the fault

- Cause of failure:Fuse failure

- Applicable models:Motion Fast 82kW

- Troubleshooting steps:

| procedure | Contents | Example (picture or reference file) |
| --- | --- | --- |
| Step1 | Disconnect the AC contactor of DC pile, and measure the on-off condition of the fuse by using the buzzer gear of multimeter. If there is a beeping sound, the fuse is normal. If there is no beeping sound, it means that the fuse is damaged, and execute Step2; |  |
| Step2 | Use a 13MM wrench to remove the fuse; |  |
| Step3 | After replacing the new fuse, repeat Step1 to measure whether the new fuse is conductive. If it is turned on, carry out a charging test again; If it is still not connected, please contact the local after-sales service team to handle it. If charging is normal, the device will return to normal; If the charging is still abnormal, please contact the local after-sales service team. |  |