IEMS Cannot Start Processing SOP

- Fault Name:IEMS fails to start

- Fault code:None yet

- Fault phenomenon:The IEMS cannot be turned on normally after powering up

- Cause of failure:

- IEMS power supply wiring error

- IEMS terminal loose

- PCS cabinet not powered on

- IEMS Internal Hardware Failure

- Applicable models:HXMS-100

- Troubleshooting steps:

| procedure | Contents | Example (picture or reference file) |
| --- | --- | --- |
| Step1 | Check the external cabinet power supply status. If the cabinet is turned off or not powered on, please power the cabinet on; If the cabinet is powered on, refer to Step2; |  |
| Step2 | Check the IEMS power terminal wiring and positive and negative poles. If the positive and negative poles are connected reversely or the screws are loose, rewire and tighten the screws; If the wiring is correct and tight, the machine still cannot be turned on, refer to Step3; |  |
| Step3 | Check the power terminal fit and host interface. If the terminal is not fully plugged in or the host interface is loose, unplug and reinforce. If the physical connection is completely normal but the device is unresponsive, and there is an internal failure in the IEMS, please replace the device. |  |