Low-volt Battery Short-circuit Treatment SOP

1. Fault Name:
· Battery Short-circuit
· Battery Voltage Abnormal
2. Fault code:
· BA1 0080, BA3 0080
· F1 0100000
3. Fault phenomenon:The battery indicator light is red, and the inverter gives a battery short-circuit alarm
4. Cause of failure:Inverter battery port short circuit
5. Applicable models:BLF 51-5
6. Troubleshooting steps:
	procedure
	Contents
	Example (picture or reference file)

	Step1
	Ensure that the positive and negative poles of the battery are not short-circuited; If short-circuited, please contact the local after-sales service team.
	

	Step2
	When the battery is not short-circuited, turn off the battery air Switch, the DC Switch of the inverter, and the mains Switch, and remove the battery power line.
	

	Step3
	Turn on the battery open again and observe the color of the battery indicator light.
If it is green, the battery is fine,The short-circuit side is determined at the inverterThe battery port of.
(Verification method: Use a multimeter, adjust it to buzz, and measure the Bat + and BAT-of the battery port of the inverter with a red and black probe;
If there is a beeping sound, it proves that the inverter battery port is short-circuited;
If there is no beep, please contact your local after-sales service team)
If the indicator light is red or not illuminated, please contact your local after-sales service team.
	



