Low-volt Battery’s SoC Low Protection Treatment SOP

- Fault Name:Low voltage battery SoC is too low

- Fault code:None yet

- Fault phenomenon:

- The machine reports that the battery voltage is too low

- Abnormal battery failure

- Cause of failure:

- BMS firmware version is too low

- Not fully charging the battery to 100% for a long time

- Failure to regularly recharge the battery

- Applicable models:BLF51-5

- Troubleshooting steps:

| procedure | Contents | Example (picture or reference file) |
| --- | --- | --- |
| Step1 | Check whether the BMS is the latest version on the monitoring platform, and if not, upgrade to the latest version. If it is already the latest version, jump to Step2; |  |
| Step2 | Check the battery SOC and cell voltage on the monitoring platform: If it is found that the battery SOC is below 10% for a long time and the single cell voltage is less than 3V but greater than 2.5, jump to Step3; If the single cell voltage is less than 2.5V, jump to Step4; |  |
| Step3 | Manually set the inverter mode to either backup mode or TOU mode to fully charge the battery to 100%. |  |
| Step4 | Refer to attached documentation:New model DC charger operation SOP，Recharge the battery. If the battery SoC value is still very low after replenishment, please contact your local after-sales service team. |  |